## Slide 1: Grid Operation Key Issues and Challenges
U K Verma
GM, ERLDC-POSOCO

## Slide 2: Contents
Typical Numbers for Indian Power System
Growth of interconnected Indian power system
  NEW-SR grid synchronization and challenges
International connections
  Power transfer to Bangladesh and Challenges
Integration of renewables
Power system in extremities

## Slide 3: Indian Power System : Amongst the Largest in the World
National Grid (UK)
61GW, 62 mln
MidWest ISO (USA)
98GW, 39 mln
RTE (France)
100GW, 65 mln
PJM (USA)
164GW, 60 mln
Red Electrica (Spain)
44GW, 46 mln
ONS (Brazil)
77GW, 189 mln
SO - UPS (Russia)
157 GW, 144 mln
Tepco (Japan)
64GW, 45 mln
KPX (South Korea)
76GW, 50 mln
Terna (Italy)
57GW, 60 mln
SGCC (China)
554GW, 1100 mln
PGCIL (India)
135 GW, 1200 mln
Eskom
(South Africa)
37 GW, 50 mln
Source: VLPGO, 2014
The information for each member refers to peak load and customers served
CSG (China)
129 GW, 240 mln

## Slide 4: Region wise Installed Generating Capacity
Captive generating capacity as on 31st March 2011 = 34,445 MW
Source: CEA website

## Slide 5: Owner wise Sector wise Breakup
Source: CEA website
All figure in MW

## Slide 6: All India installed capacity breakup

## Slide 7: Indian Power System (upto 132/110 kV level)
System Components | NEW Grid | SR Grid | Total(N-E-W-S)
Nodes | 4450 | 1335 | 6317
Generating Plants | 492 | 237 | 733
Machines | 1327 | 532 | 1862
Branches | 9031 | 3317 | 12348
Transformers | 1965 | 650 | 2615
Bus reactors | 197 | 46 | 243
Line reactors | 419 | 79 | 498
Voltage Level (in kV) | Central Sector | State Sector | JV/Pvt | Total
765 | 7771 | 411 | -- | 8182
400 | 79265 | 34685 | 8370 | 122320
220 | 10474 | 133413 | 830 | 144717
+- 500 Kv HVDC lines | 5948 | 1504 | 1980 | 9432
As on 31st March 2014
Line lengths in Ckt. Km.

## Slide 8: Some Typical Numbers …
All India Installed Capacity :~ 243 GW
Peak Demand met :~ 129 GW
Max Wind Generation :~ 224 MU
Generation outage :~ 27000 MW
Energy : ~ 2650 MU/day
Hydro generation :~ 375 MU/day
400kV & above Trans. Line :~ 780 nos
Short Term Open Access :~ 240 MU/day
  Power Exchange volume : ~ 80 MU/day
  Bilateral volume : ~ 160 MU/day
Average figures

## Slide 9
Arial view of Indian subcontinent in Night
High load
density
Resource rich areas
Spatial Distribution Of Load

## Slide 10
NEW Grid
South
Grid
South
West
North
East
Northeast
Five Regional Grids
Five Frequencies
October 1991
East and Northeast
synchronized
March 2003
West synchronized
With East & Northeast
August 2006
North synchronized
With Central Grid
Central Grid
Five Regional Grids
One Frequencies
Target 2020: 292 GW
MERGING
OF
MARKETS
Renewable: 31 GW
Installed Capacity: 243 GW
Inter – Regional
Capacity:
35 GW
North East West
Grid
All India Grid
31st December 2013
NEW grid synchronized
with SR grid

## Slide 11: Why Integration? Obvious Benefits of Integrated Operation
Security
Reliability and quality of supply
  Suppression of frequency and voltage fluctuations
Sharing of resources
  Reduction in investment and conservation
  Economies of scale – Funding, Staggered Capacity
  Utilisation of diversities
  Environmental dispatch & new plant siting
  Coordination of maintenance schedules
Risk sharing
Merit order operation
Economical exchange of electric power

## Slide 12: NEW and Southern Region Grid Synchronization

## Slide 13
KOLAR
TALCHER
SOMANAHALLI
GOOTY
NELLORE
THIRUVALAM
NELAMANGALA
HIRIYUR
WARDHA
RAIPUR
PARLI
SHOLAPUR
LONIKHAND
SR
ER
WR
400 kV Line
500 kV HVDC Line
GAJUWAKA
BHADRAWATI
RAICHUR
ROURKELA
765 kV Line
STERLITE
RAIGARH
PUNE
400 kV Under construction Line
765 kV Under construction Line
AURANGABAD
KURNOOL
YELHANKA
MADHUGIRI
BIDADI
NAG’SAGAR
SALEM
Existing/Upcoming Network
VIJAYAWADA
SHOLINGANALLUR
Transmission line in WR
765 kV Raipur-Warda D/C
765 kV Warda-Aurangabad D/C
400 kV Aurangabad-Pune D/C
400 kV Pune-Parli D/C
Transmission line in SR
765 kV Raichur-Kurnool S/C
765 kV Kurnool Thiruvalam D/C
400 kV Vijaywada-Nellor D/C
400 kV Nellor-Thiruvalam D/C
400 kV Gooty-Madhugiri D/C

## Slide 14: Successful synchronization of Southern Grid on 31st Dec 2013 at 20:25 hours (through 765 kV Raichur (SR)- Solapur (WR) S/C)

## Slide 15: Synchronization of SR grid with NEW grid at 2025hrs on 31.12.13
328 MW
-191 MW

## Slide 16
Instant of Synchronization at 2025 hrs.
Frequency Oscillations for 16s
Frequency difference of 0.034 Hz at the instant of Synchronization

## Slide 18
Up to 700 MW flow on 765 kV Sholapur-Raichur line in either direction
Re-synchronization at 20:23 hours on 2nd Jan’14
Re-synchronization at 1754hrs on 07.01.14
Re-synchronization at 19:56 hours on 8th Jan’14
Re-synchronization at 11:53 hours on 14th Jan’14
1st synchronization at 20:25 hrs on 31st Dec 2013
Re-synchronization at 10:41 hours on 5th Jan’14
Tripping of line on overcurrent at 05:33 hours on 2nd Jan’14
Tripping due to Raichur ICTs at 18:23 hours on 4th Jan’14
Tripping due to Raichur ICTs at 12:54 hours on 5th Jan’14
Tripping at 2130hrs on
7th Jan’14 on overcurrent
Manually Opened at 0732 hrs on 10th Jan’14 during Talcher-Kolar HVDC Shutdown

## Slide 19
765kV Raichur-Sholapur Flow Ramp Rate (MW/Min)

## Slide 20: HVDC Set-point Variation
HVDC set-point variation was possible with STOA curtailment

## Slide 21
Chart: 
Hz
%

## Slide 22: Observations
Load and Generation changes in any of the regional grids leads to variation in line flow on 765 kV Sholapur-Raichur.
  Variable from +800 MW to -600 MW
  200 MW/minute ramp rate of SR load hour boundary
  Oscillations under observation………..uncharted territory
  5th harmonic increase observed at Bhadrawati
System currently operating with System Protection Schemes (SPS) and operator substituting for
  Primary response, secondary response as well as weaknesses in the transmission system

## Slide 23: Challenges … (1)
Sudden increase in flow on 765kV Raichur-Sholapur flow leading to SPS operation.
    Hourly load changeover
    Intermittent nature of Wind generation in SR
    Tripping of largest unit in SR
Frequent synchronization & de-synchronization
Data telemetry
Frequent HVDC set-point toggling and STOA Curtailments

## Slide 24: Challenges … (2)
Operation of defense plans (SPS and UFR)
Expectations of stakeholders for scheduled interchange of power on Raichur-Sholapur 765kV
More parallel AC corridors required
Frequency Band Tightening (tighten to 49.9 to 50.05 Hz from 17th Feb 2014) and Primary response
Line loading being controlled through
  Sensitizing SR states to regulate their generation and load meticulously to minimize impact on line loading
  Regulating flow on HVDC links to SR
  Keeping margins in the transmission for contingencies

## Slide 25: Challenges … (3)
Twenty five (25) identified transmission elements to be expedited
  Only three (3) elements commissioned so far.
  Second 765 kV Sholapur-Raichur line by RSTCL required.
Implementation of the Unified Real Time Dynamic State Measurement System (URTDSM) project
Grid Security Expert System (GSES)
Secondary control through Automatic Generation Control or AGC as being adopted by large grids

## Slide 26: Peculiarities of Regional Grids in India
SOUTHERN REGION
WESTERNREGION
EASTERN REGION
NORTHERN REGION
NORTH-EASTERN REGION
REGIONAL GRIDS
Deficit Region
Snow fed – run-of –the –river hydro
Highly weather sensitive load
Adverse weather conditions: Fog & Dust Storm
Very low load
High hydro potential
Evacuation problems
Industrial load and agricultural load
Low load
High coal reserves
Pit head base load plants
High load (40% agricultural load)
Monsoon dependent hydro
CHICKEN-NECK
Notes: June 27, 2014
NRLDC
26

## Slide 27: Peculiarities of Indian Power System
Skewed resource distribution
Long-haulage of power
Resource Inadequacy
Weather extremes
Diversity

## Slide 29: Inter-regional Transfer Capacity
12,130 MW
1,260 MW
6,490 MW
8,720 MW
3,620 MW
3,630 MW
SOUTHERN REGION
WESTERNREGION
NORTHERN REGION
NORTH-EASTERN REGION
EASTERN REGION

## Slide 30
765 KV RING MAIN SYSTEM THE POWER ‘HIGHWAY’
HYDRO POWER FROM THE NORTH-EAST & CHEAP PIT HEAD THERMAL POWER FROM THE EAST ENTERS THE RING AND EXITS TO POWER STARVED REGIONS
HYDRO

## Slide 31: 765 KV ring under construction
NR
WR
SR
ER
NER
1
2
3
4
5
8
7
6
Agra
Gwalior
Bina
Seoni
Sipat
Ranchi
Balia
Fatehpur

## Slide 32
LUCKNOW
MOGA
2 x1500 MVA ICT
2 x 240 MVAR B/R
240 MVAR L/R
* USED AS B/R
GAYA
3 x1500 MVA ICT
2 x 240 MVAR B/R
240 MVAR L/R
SIPAT
2 x1000 MVA ICT
2 x 240MVAR L/R
240 MVAR B/R
3 x1500 MVA ICT
240 MVAR B/R
2 x 240 MVAR L/R
2 x1500 MVA ICT
2x 240 MVAR B/R
240 MVAR L/R
2 x1500 MVA ICT
240 MVA L/R
2x 240 MVAR B/R
765kV charged at 400kV
765kV charged at 765kV
400kV
Present 765kV GRID MAP
WARDHA
BILASPUR
GWALIOR
BALIA
FATEHPUR
BINA
2 x1000 MVA ICT
5 x 240MVAR L/R
1x 240 MVAR B/R
SEONI
INDORE
ANPARA C
2 x1000 MVA ICT
189 MVAR B/R
330 MVAR L/R
2 x1000 MVA ICT
189 MVAR B/R
330 MVAR L/R
2 x1500 MVA ICT
240 MVAR B/R
240MVAR L/R
3 x1500 MVA ICT
240 MVAR B/R
2x 240 MVAR L/R
1 x 1500 MVA ICT
1 x 330 MVAR B/R
2 x1500 MVA ICT
330 MVAR B/R
2 x 330 MVAR L/R
3 x1500 MVA ICT
240 MVAR B/R
3x 240 MVAR L/R
2 x 240MVAR L/R(Fut.)
BHIWANI
2 x1000 MVA ICT
2 x 240 MVAR B/R
SATNA
2 x1000 MVA ICT
2 x 240MVAR L/R
240 MVAR B/R
UNNAO
335 kM
409 kM
316 kM
I - 274 kM
II - 276 kM
I – 268 kM
292 kM
II - 261 kM
I - 337 kM
I - 22 kM
II - 338 kM
II - 22 kM
I – 310 kM
I – 273 kM
I - 129 kM
I - 234 kM
II- 128 kM
II- 235 kM
JHATIKARA
*
4x1500 MVA ICT
1x 240 MVAR B/R
1x 240 MVAR L/R
85 kM
AGRA
245 kM
MEERUT
Future
2 x1500 MVA ICT
1 X 240 MVAR B/R
243 kM
1 x1000 MVA ICT
SASAN
246 kM
2 x1500 MVA ICT
2 x 240 MVAR L/R
145 kM
340 kM
330 MVAR Mid
Point REACTOR
SASARAM
RANCHI
2 x1500 MVA ICT
1 x 240MVAR L/R
240 MVAR B/R
SOLAPUR
2 x1500 MVA
2 x1500 MVA ICT
RAICHUR
303 kM
208 kM
Dharamjaygarh

## Slide 33: Transmission technology
Issues:
  Reactive Compensation in EHV/UHV
  Importance of lines of all voltage levels
  Short Circuit Levels

## Slide 34
Chart: 
| 1992-93 | 1993-94 | 1994-95 | 1995-96 | 1996-97 | 1997-98 | 1998-99 | 1999-2000 | 2000-01 | 2001-02 | 2002-03 | 2003-04 | 2004-05 | 2005-06 | 2006-07 | 2007-08 | 2008-09 | 2009-10 | 2010-11 | 2011-12 | 2012-13 | 2013-14
Energy in MU | 1015 | 2995 | 1416 | 1756 | 1779 | 3637 | 5888 | 7740 | 8586 | 11539 | 12615 | 22783 | 30763 | 34816 | 38211 | 42932 | 46027 | 52374 | 56747 | 58999 | 65860 | 78384
Inter Regional Exchange
Energy in MU

## Slide 36: International Connections

## Slide 37: International Connections
Bhutan
  Tala HEP (1020 MW) – 400 kV
  Chukha HEP (336 MW) – 220 kV
  Kurichu HEP (60 MW) – 132 kV
  Net import by India
Nepal
  Over 16 links of 132/33/11 KV
  Net export to Nepal (about 10% of Nepal’s demand)
Bangladesh
  500 MW B-t-B HVDC at Bheramara (Bangladesh)
  400 kV Berhampur (India) –Bheramara (Bangladesh) D/C
  LILO of Farraka-Jeerat at Bheramara
  Net export to Bangladesh
Future
  SAARC Grid
37

## Slide 38: Transnational links between ER and Nepal
132 kV Valmikinagar-Surajpura(Nepal) S/C
132 kV Kataiyya(GSS)-Duhabi(Nepal) S/C
33 kV Kataiya-Rajbiraj (Nepal) S/C
33 kV Kataiya-Biragram (Nepal) S/C
33 kV Sitamarhi-Jaleshwar (Nepal) S/C
33 kV Rauxsaul-Birganj (Nepal) S/C
33 kV Jaynagar-Sirha (Nepal) S/C

## Slide 39: SAARC Grid
Bhutan
Nepal
India- Bhutan synchronous links
400 kV Tala-Binaguri D/C
400 kV Tala-Malbase-Binaguri
220 kV Chukha-Birpara D/C
220 kV Chukha-Malbase-Birpara
132 kV Kurichu-Gelegphug-Bongaigaon
Over 16 links of 132/33/11 KV Radial links with Nepal Net import by Nepal
Future Connections with Sri Lanka
India- Bangladesh asynchronous links
400 kV Bheramara (Bangladesh)–Berhampur (India) D/C
500 MW B-t-B HVDC at Bheramara (Bangladesh)
Bangladesh

## Slide 40
ASYNCHRONOUS INTERCONNECTION WITH BHUTAN

## Slide 41: Power Transfer to Bangladesh
Present status
  400 kV D/C from Berhampur-Bheramara (Bangladesh)
  500 MW B-t-B HVDC terminal at Bhermara (Bangladesh)
  Started in month of October 2013
  Initially power transfer was restricted to 250 MW
  With commissioning of SPS (system protection scheme) power transfer is enhanced to 500 MW
Proposed lines
  400 kV HTSL (high tensile low sag) D/C line from Sagardighi-Berhampur.
  Proposed for reliable supply of 500 MW to Bangladesh through out the year.

## Slide 42: Power Map of Bangladesh

## Slide 44: Line Flows(in MW)

## Slide 45
Voltage (in kV)

## Slide 46: Jeerat Voltage (Sep’13 – Dec’13)

## Slide 47
Bheramara Voltage (in kV)

## Slide 48: Special Protection scheme (SPS) to take care of contingency situation

## Slide 49: SYNCHRONOUS INTERCONNECTION WITH BHUTAN
2 x 139 + 2 x 144 kms. of
400 kV lines in Bhutan
Snapshot from National Power System Desk
TALA HEP 1020 MW (6x170 MW)
(BHUTAN)
DELHI
BARELI
LUCKNOW
UNNAO
GORAKHPUR
MUZAFFARPUR
PURNEA
BINAGURI
EASTERN GRID
NORTHERN GRID
3200 CIRCUIT KILOMETERS TALA TRANSMISSION SYSTEM

## Slide 51
A fairly good Fuel Mix

## Slide 52: Integration of Renewable Generation

## Slide 53
SOLAR ENERGY MAP OF INDIA
WIND ENERGY MAP OF INDIA
Unevenly Distributed Renewable Resources

## Slide 54: Potential of Renewable Energy in India (MW)
54
Source | Potential | Installed Capacity
Wind | 49000 | 20298
Biomass | 17000 | 1286
Small Hydro (< 25 MW) | 15000 | 3774
Co-generation- Bagasse | 5000 | 2512
Waste | 2700 | 99
Solar | > 100,000 | 2208
Source : MNRE as on 31st Jan 2014
Notes: 54

## Slide 55: Fluctuations in Wind Generation
TIME
MW
DATE
For Tamil Nadu
Aug 2010

## Slide 56: Fluctuations in Wind Generation
TIME
MW
DATE
For Gujarat
Aug 2010

## Slide 57: Renewable Integration
Key Challenges
  High Capital Cost
  Intermittency of Generation
  Forecasting techniques
  Separate control desk for renewables
  Having ancillary services in place
Standards for renewable integration
  Fault Ride Through Capability
  High Frequency Tripping
High Capacity Corridors for Renewable evacuation
  Evacuation through HVDC
  National Transmission Highway from TN to Rajasthan

## Slide 58: Power System in Extremes

## Slide 59: UNPRECEDENTED SNOWFALL AND BLIZZARD
PIR PANJAL
MOUNTAIN RANGE
400 kV
Kishenpur-Wagoora
was commissioned on
31st Oct-2006
220 kV
Kishenpur-Pampore
174 km
12 meters of snowfall in Feb 2005,
Highest snowfall in last 30 years.
Previous highest of 4.5 meters was
recorded in February 1967.
105 km
180 km
Notes: The longest time for which the Kashmir island operated continuously was 2 hours and 15 minutes on 13th Feb 2005.
At 1832 hrs of 08th February 2005, the towers of 220 kV Kishenpur-Pampore D/C line at location number 38, 39, 44 and 45 near Peer Panjal area (90 km from Srinagar) collapsed and the valley plunged into darkness as the power supply to the valley was cut-off. The tower location was inaccessible due to heavy snowfall. The tower location was inaccessible due to heavy snowfall. Line restoration through ERS was ruled out due the risk of avalanches. The closure of the Jammu-Srinagar highway compounded the problems and made the restoration and relief work almost impossible.
The parallel operation through the 132 kV single circuit continued for several weeks till the 220 kV Kishenpur-Pampore line was restored on 07th March 2005. The conductors of 220 kV Kishenpur-Pampore line near the damaged tower were buried under the snow and the line had be restored using the Panther conductors (instead of Zebra conductors used in 220 kV lines) of the unused 132 kV Udhampur-Batote-Wampoh S/C. This amounted to a reconfiguration of Kishenpur-Pampore line wherein the towers of 132 kV Udhampur-Batote-Wampoh were also used. The original configuration was later restored in August 2005.
400 kV Kishenpur-Wagoora commissioned in

## Slide 60: IMPACT OF SILT ON GRID OPERATION
SILT DEPOSITS
SPITI RIVER

## Slide 61
CHANGE OF KOSI RIVER COURSE

## Slide 62
Original river course
Changed river course
CHANGE OF RIVER COURSE

## Slide 63
TOWER COLLAPSE DUE TO
SHIFTING OF RIVER

## Slide 64: UNFORESEEN LOAD CRASH 8 HOUR TEST OF NERVES

## Slide 65: ‘Killer Smog’

## Slide 66: ‘Killer Smog’
Chart: SMOG AFFECTED GRID-DAYS IN NORTHERN REGION
| 1995-00 | 2000-05 | 2005-06 | 2006-07 | 2007-08
East | 2 | 2 | 2 | 11 | 12

## Slide 67
Phailin cyclone(12-Oct-2013), Huge Demand crash in Eastern Region in very short time
Demand crash of around 2000 MW in Odisha
26 Substation got affected
45 lines affected
220 kV Narendrapur-Mendasal-II still under breakdown

## Slide 68: Thank You !!